Keltech Incorporated
Electric Tankless Commercial Water Heaters HL Series
Guide Specification

Keltech, Inc. Tankless Commercial Heaters are designed to accommodate most commercial fluid heating applications including: environments where demand is < 18kW and total flow is ≤ 7 GPM (26.5 L/m), and environments where lower activation flows are required: standard units are 0.5 GPM (1.9 L/m) with options as low as 0.15 GPM (0.6 L/m). HL-Series units are also suited to applications where only single phase service is available or 3-Phase 208V, 240V, or 480V. HL Series products include a NEMA 1 enclosure as standard, with NEMA 4 and 4X options available.

Keltech's commercial water heaters allow water supply to quickly reach the required set point temperatures 40 - 160 deg. F (4.4 – 71.1 deg. C) and provide continuous flow of heated water – up to 7 GPM (26.5 L/m).

Keltech's PID Temperature Controller is more energy efficient and reliable than traditional microprocessors using staged elements. Power is infinitely variable, with no fixed inputs. The PID controller makes it possible to modulate the amount of power applied to the elements while also dispersing the required power evenly across all elements. This unique feature increases the product's life cycle.

View Keltech's complete line of innovative tankless water heaters for, continuous flow in industrial, healthcare and laboratory facilities, and specialty applications, at www.keltech-inc.com.  Contact Keltech, Inc., Delton MI; Phone: (800) 999-4320) Email sales@keltech-inc.com.

Keltech eases the specifying process with a seasoned customer service staff and a range of helpful information tools on an advanced website. Keltech is a subsidiary of Bradley, the industry leader in the manufacture of safety eyewash, eye/face wash, and eyewash heaters, as well as premium quality commercial plumbing fixtures, valves, TMVs, electric tankless water heaters and washroom accessories that appear in the following CSI MasterFormat 2012™ Sections:

Section 22 11 19 - DOMESTIC WATER PIPING SPECIALTIES (Thermostatic mixing valves)

Section 22 33 13 - INSTANTANEOUS ELECTRIC DOMESTIC WATER HEATERS 
(Keltech tankless water heaters)

Section 22 42 16.11 - COMMERCIAL SINKS AND FAUCETS

Section 22 42 23 - COMMERCIAL SHOWERS AND SHOWER VALVES

This document is Copyright© 2014 Bradley Corporation

SECTION 22 33 13 – INSTANTANEOUS ELECTRIC DOMESTIC WATER HEATERS

GENERAL

SECTION INCLUDES

Electric, tankless commercial water heaters and water heater accessories.

Specifier: If retaining optional "Related Sections" article, edit to include sections applicable to Project.

RELATED SECTIONS

Division 22 Section "General-Duty Valves for Plumbing Piping" for valves.

Division 22 Section "Domestic Water Piping" for water piping.

Division 22 Section "Domestic Water Piping Specialties" for vacuum breakers, water pressure-reducing valves, water-hammer arresters, and specialty valves.

Division 26 Sections for electrical power and control wiring.

Specifier: If retaining optional "References" article, edit to include standards cited in edited Section.

REFERENCES

General: Applicable edition of references cited in this Section is current edition published on date of issue of Project specifications, unless otherwise required by building code in force.

American National Standards Institute (ANSI) http://webstore.ansi.org:

ANSI 372 – Drinking Water System Components – Lead Content

American Society of Sanitary Engineering (ASSE): www.asse-plumbing.org

ASSE 1003 - Performance Requirements for Water Pressure Reducing Valves for Domestic Water Distribution Systems

        - ASSE 1010 - Performance Requirements for Water Hammer Arresters National Electrical Manufacturers Association (NEMA) www.global.ihs.com:

NEMA Standards Publication 250 - Enclosures for Electrical Equipment (1000 Volts Maximum)

National Fire Protection Association (NFPA) www.nfpa.org:

          - NFPA 70 - National Electrical Code

NSF International

NSF 61 - Drinking Water System Components – Health Effects

NSF 372 - Drinking Water System Components - Lead Content

Underwriters Laboratories (UL) www.ul.com:

UL 499 - Standard for Electric Heating Appliances

ACTION SUBMITTALS

Product Data: For each product:

Manufacturer's data sheets indicating unit performance and compliance with requirements.

Include details of electrical and mechanical operating parts.

Show mounting and securing requirements and utility connection requirements.

INFORMATION SUBMITTALS

Specifier: Retain paragraphs below when Project requirements include compliance with Federal Buy American provisions.

Buy American Act Certification: Submit documentation certifying that products comply with provisions of the Buy American Act 41 U.S.C 10a – 10d.

Source quality-control test reports.

Field quality-control test reports.

CLOSEOUT SUBMITTALS

Operation and maintenance data.

QUALITY ASSURANCE

Source Limitations: Obtain electric tankless water heaters through a single source from a single manufacturer.

Electrical Components: Listed and labeled per NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

        - Lead-Free Construction:  Comply with NSF 372 for fixture components in contact with potable water.

Standard Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of electric, domestic-water heaters that fail in materials or workmanship within specified warranty period.

          - Warranty Period:  From Date of Substantial Completion

##### Electrical Components, two years

##### Heating Elements, four years

##### Heat Exchanger Free From Leaks, eight years

PRODUCTS

MANUFACTURERS

Basis-of-Design Product: Subject to compliance with requirements, provide electric tankless commercial water heaters by Keltech, Inc., Delton MI; Phone: (269) 623-6395; Email sales@keltech-inc.com; Web site www.keltech-inc.com.

Submit requests for substitution in accordance with Instructions to Bidders and Division 01, General Requirements.

ELECTRIC, TANKLESS COMMERCIAL WATER HEATERS

Electric tankless commercial water heater, UL 499, sized for low flow constant temperature requirements, with PID Controller, liquid-cooled triac switches, low flow activation, and overheat protection.

Basis of Design Manufacturer/Model: Keltech, Inc., Model HL Commercial Water Heater.

Specifier: Select one of three "Enclosure" subparagraphs.

Enclosure: [0.052-inch/18-ga.- (1.32-mm-) thick galvanized steel, NEMA 1].

Enclosure: [0.052-inch/18-ga.- (1.32-mm-) thick, NEMA 4] [0.063-inch/16-ga.- (1.59-mm-) thick stainless steel NEMA 4X].

Heat Exchanger: Copper tubing with brazed brass fittings and large internal passageways for minimal pressure drop. NSF 61 barrier materials for potable water, without storage capacity.

Specifier: Select following subparagraph for applications requiring contact with food or deionized water.

            - Xylan Fluoropolymeric Coating: FDA approved for food contact or deionized water

High Temperature Package: [Insert temperature required between 160 and 190 deg. F] [Not required].

Connections: [3/4 inch copper sweat inlet, outlet NEMA 1] [3/4 inch female NPT inlet, outlet NEMA 4] [3/4 inch female NPT inlet, outlet NEMA 4X].

Rating: 150 psig (1035 kPa).

Heating Element: Heavy duty, low-watt density Incoloy 800 sheathed resistive element

Temperature Control: Microprocessor with PID logic and dual display of set-point and actual outlet water temperature.

Safety Controls:

Surface mounted bi-metal thermostat with manual reset.

Mounting: Wall mounted.

Capacity:

Specifier: If temperature rise/flow rate data appear on Drawings, then select "As scheduled" option. Otherwise, insert temperature rise and flow rate below from product data sheet. Temperature rise range available: 10 – 140 deg. F (6 – 78 deg. C). High Temperature Option Setpoints Available: 160 - 190 deg. F (71.1 – 87.8 deg. C). Flow range available: 0.75 - 15 gpm (1.9 - 57 L/m).

Temperature Rise at Flow Rate: [___ deg F (__ deg C) at ___ gpm (__ L/m)] [As scheduled].

Adjustable Temperature Setpoint: [___ deg F (___ deg C)] [As scheduled].

Electrical Characteristics:

5 kW at [208VAC/1-phase] [240VAC/1-phase] [As scheduled].

6 kW at [208VAC/1-phase] [240VAC/1-phase] [277VAC/1-phase] [480VAC/1-phase] [As scheduled].

10 kW at [208VAC/1-phase] [240VAC/1-phase] [208VAC/3-phase] [480VAC/3-phase] [As scheduled].

12 kW at [208VAC/1-phase] [240VAC/1-phase] [277VAC/1-phase] [480VAC/1-phase] [As scheduled].

15 kW at [208VAC/1-phase] [240VAC/1-phase] [208VAC/3-phase] [480VAC/3-phase] [As scheduled].

18 kW at [208VAC/1-phase] [240VAC/1-phase] [277VAC/1-phase] [480VAC/1-phase] [208VAC/3-phase] [240VAC/3-phase] [480VAC/3-phase] [As scheduled].

Specifier: Retain one or more of the following three subparagraphs that describe available options for the HL Series models if required for Project.

Facility Controls Integration: 4: 20 mA input [NEMA 4] [stainless steel NEMA 4X].

Specifier: Optional temperature lockout range available: 40 - 160 deg. F (5 - 71 deg. C).

Temperature Lockout:  ____ deg. F (____ deg. C).

Low Flow Activation:  [0.15 GPM (0.6 L/m)] [0.25 GPM (0.9 L/m)].

WATER HEATER ACCESSORIES

Provide electric tankless water heater system including the following system accessories:

Specifier: Retain accessories required for project from those in four paragraphs below; coordinate with contents of other Division 22 sections.

Pressure and Temperature Relief Valves: Pressure and Temperature Relief Valves: [Brass] [Stainless steel, ASME rated and stamped pressure relief valve]. Adjust to pressure setting less than water heater working-pressure rating.

Pressure and Temperature Safety Relief Valve set to 80 psig (552 kPa).

Pressure-Reducing Valves: ASSE 1003.

Vacuum Relief Valves: ANSI Z21.22/CSA 4.4.

Shock Absorbers: ASSE 1010 or PDI-WH 201, Size A water hammer arrester.

Thread Adapters: NPT to BSPP, stainless steel.

Y-Strainer: [Lead Free Brass] [Stainless steel].

EXECUTION

INSTALLATION

Electric, Tankless, Domestic-Water Heater Mounting:

Install water heaters in accordance with manufacturer's written instructions.

Install water heaters level and plumb, according to layout drawings and referenced standards.

Maintain manufacturer's recommended clearance and access dimensions.

Install water supply piping to each water heater, and from heater to fixture requiring hot water supply connection.

          - Install stop valves on water supply and outlet piping. Provide stop valve on each supply in readily-serviced location. Lock stop valve in OPEN position.

          - Comply with Division 22 Section, General-Duty Valves for Plumbing Piping, for stop valve requirements.

If shipped loose, install pressure and temperature safety relief valves on water heater. Run relief valve discharge lines as shown in manufacturer's instructions.

Extend relief-valve outlet line, and discharge by positive air gap above closest floor drain.

Install relief valve drain piping as indirect waste to spill by positive air gap into open drains or over floor drains. Install hose-end drain valves at low points in water piping.

Run relief valve drain piping without creating tripping hazard.

FIELD QUALITY CONTROL

Do not energize water heater until hydrostatic testing of domestic water lines is complete. See Division 22 Section "Domestic Water Piping."

Test and adjust installation.

Set field-adjustable temperature set point of temperature-actuated controls. Adjust set point within allowable temperature range.

Replace defective or malfunctioning controls and equipment.

Clean unit surfaces, test fixtures, and leave in ready-to-use condition.

END OF SECTION